## 0102 A系UPW(橫)
Tag NO | UPWAAIA-01A | UPWAPHIA-01A | UPWAFWA T1 | UPWAFWA LG-1 | UPWAFWA PG-1 | UPWAFWA FI-01 | UPWAFWA PG-2 | UPWAFWA PG-3 | UPWAFWA LG-2 | UPWAFWA PG-4 | 2B3TA FI-3 | 2B3TA FI-4 | 2B3TA PG-6 | 2B3TA PG-7 | 2B3TA LGS-1 | 2B3TA PG-8 | 2B3TA FI-5 | 2B3TA FI-6 | 2B3TA PG-9 | 2B3TA PG-10 | 2B3TA AIA-1 | 2B3TA FQA-1 | UPWADIL1A | UPWADI PG-12A | UPWADI FI-7A | UPWADI PG-14A | UPWADI PG-15A | UPWADI PIA-1A | 2B3TA LG-11 | 2B3TA LG-7 | 2B3TA LG-8 | 2B3TA LG-9 | 2B3TA PG-16 | 2B3TA PG-17 | 2B3TA TA-11 | 2B3TA TA-12 | 2B3TA PG-13 | 2B3TA FI-8 | 2B3TA FI-9 | 2B3TA TICA-1 | 2B3TA FWQ1 | UPWARO LIA-30A | UPWARO PG-35A | UPWARO PG-36A | UPWARO PIA-30A | UPWARO PG-30A | UPWARO FI-30A | UPWARO PG-31A | UPWARO FI-31A | UPWAUPWA PG-32 | UPWAUPWA PG-33 | UPWATICA-30 | UPWADI FI-50A | UPWA PG-50 | UPWA PG-51 | UPWA FDP | UPWA PS-50 | UPWA PG-52 | UPWA PG-53 | UPWA PS-51 | UPWA PG-54 | UPWA PG-55 | UPWA PG-56 | UPWA PG-57 | UPWA PG-58 | UPWA FI-51 | UPWA FI-52 | UPWA AIA-50 | UPWA CPA | UPWA FI-53 | UPWA PG-59 | UPWA PG-60 | UPWA PG-61 | UPWA AIA-51 | UPWA CPWOA | UPWA FI-54 | UPWA PG-62 | UPWA PG-63 | UPWA PG-64 | UPWA PG-65 | UPWA FI-55 | UPWA PG-66 | UPWA PG-67 | UPWA AIA-52 | UPWA CPPOA
項目 | UPWA原水 導電度 | UPWAA原水 pH 值 | UPWAA原水 溫度 | UPWA原水儲槽液位 | UPWA原水 Pump 出口壓力 | UPWA原水 流量 | UPWA凝集過濾器入口 壓力 | UPWA凝集過濾器出口 壓力 | UPWA濾過水槽液位 | UPWA濾過水 Pump 出口壓力 | CATION 塔入口流量 | CATION 塔注水流量 | CATION 塔入口壓力 | CATION 塔出口壓力 | 脫碳酸塔水液位 | 中間水 Pump 出口壓力 | ANION 塔入口流量 | ANION 塔注水流量 | ANION 塔入口壓力 | ANION 塔出口壓力 | ANION 塔出口水導電度 | ANION 塔出口流量積算計 | UPWA脫鹽水槽液位 | UPWA脫鹽水 Pump 出口壓力 | UPWA脫鹽水 Pump 出口流量 | UPWA脫鹽水槽 N2 元壓 | UPWA脫鹽水槽 N2 入口壓力 | UPWA脫鹽水槽 N2 壓力 | 再生用水槽水位 | HCL儲槽液位 | NaOH儲槽液位 | PH調整-NaOH儲槽液位 | 加熱蒸氣元壓 | 加熱蒸氣入口壓力 | HCL計量槽液位(再生時) | NaOH計量槽液位(再生時) | 再生用水Pump出口壓力 | HCL Ejector稀釋水量 | NaOH Ejector稀釋水量 | NaOH 稀釋水溫度 | 2B3T自來水入口累積量 | UPWA RO處理水槽水位 | UPWA RO處理水槽N2元壓 | UPWA RO處理水槽N2入口壓力 | UPWA RO處理水槽壓力 | UPWAPROCESS系送水pump出口壓力 | UPWAPROCESS系送水pump出口流量 | UPWA洗淨系送水pump出口壓力 | UPWA洗淨系送水pump出口流量 | UPWA洗淨系使用回水壓力 | UPWAPROCESS系使用回水壓力 | UPWA冷卻熱交換器回水出口溫度 | UPWA脫鹽水流量 | 保安FILTER入口壓力 | 保安FILTER出口壓力 | 保安FILTER 壓力差 | R.O pump入口壓力SV/PV | R.O pump出口壓力 | R.O unit 入口壓力 | R.O unit 出口壓力設定值 | R.O unit 出口壓力 | R.O unit 第一段濃縮水壓力 | R.O unit 第二段入口壓力 | R.O unit 第二段濃縮水壓力 | R.O unit 第三段濃縮水壓力 | R.O unit 生產水流量 | R.O unit 濃縮水流量 | R.O unit 出口水質 | CATION POLISHER 出口水質 | 洗淨系送水 R.O 處理水流量 | 洗淨系C.P 入口壓力 | 洗淨系最終FILTER 入口壓力 | 洗淨系超純水送水壓力 | 洗淨系超純水送水水質 | 洗淨系C.P 出口水質 | PROCESS系送水R.O處理水流量 | PROCESS系C.P 入口壓力 | UF unit 入口壓力 | PROCESS系超純水送水壓力 | UF unit 濃縮水壓力 | UF unit 濃縮水流量 | UF濃縮水 FILTER 入口壓力 | UF濃縮水 FILTER 出口壓力 | PROCESS系超純水送水水質 | PROCESS系C.P 出口水質
管理值 | <600 | 6~9 | 15~35 | 500~1500 | 0.1~0.25 | 6~10 | <0.2 | <0.2 | >6 | 0.3~0.6 | 5~8 |  | <0.4 | <0.4 | 300~500 | <0.4 | 6~10 |  | <0.25 | <0.2 | <10 | <100 | V~H | 0.6~0.8 | 6~10 | <0.7 | 0.2~0.3 | -50~100 | >1500 | >300 | >300 |  | 0.5~0.7 |  | 0~600 | 0~420 | 0~0.35 | 1.6~2.4 | 2.8~3.2 |  |  | 30~95 | 0.5~5.0 | 0.1~0.3 | -50 ~ 100 | 0.6~0.9 | 8~12 | 0.3~0.7 | 9~14 | 0.2~0.4 | 0.1~0.35 |  | 0~8 | 0.05~0.3 | 0.05~0.3 | <0.1 | >0.2 | 1.5~2.5 | 0.5~1.5 | <5 | <0.3 | 0.5~1.5 | 0.5~1.5 | 0.3~1.5 | 0.3~1.5 | 4~8 | 0.4~1.2 | >1 | >1 | 8~14 | 0.2~0.5 | 0.1~0.4 | 0.1~0.4 | >18 | >18 | 8~12 | 6~8 | 0.4~0.5 | 0.3~0.5 | 0.3~0.5 | 0.5~1.5 | <0.3 | <0.2 | >18 | >18
單位 | us/cm |  | oC | mm | MPa | m3/h | MPa | MPa | m3 | MPa | m3/h | m3/h | MPa | MPa | mm | MPa | m3/h | m3/h | MPa | MPa | us/cm | m3 | mm | MPa | m3/h | MPa | MPa | mmH2O | mm | mm | mm | cm | MPa | MPa | mm | mm | MPa | m3/h | m3/h | oC | m3 | % | kg/cm2 | MPa | mm | MPa | m3/h | MPa | m3/h | MPa | MPa | oC | m3/h | MPa | MPa | MPa | MPa | MPa | MPa | kg/cm2 | MPa | MPa | MPa | MPa | MPa | m3/h | m3/h |  |  | m3/h | MPa | MPa | MPa |  |  | m3/h | kg/cm2 | MPa | MPa | MPa | m3/h | MPa | MPa