## 1101 ( N2 發生器 )(橫)
TAG. NO | COMP2FOX | COMP2FPG1 | COMP2FRUNh | COMP2FENT1 | COMP2FRUNPG1 | COMP2FOILPG1 | COMP2FVENTT1 | COMP2FINT1 | COMP2FVENTT2 | COMP2FOILT1 | COMP2FALAOX | COMP2FOSOX | COMP2FOSPG1 | COMP2FDRAINOX | COMP2FDRYOX | N2PSA1FI-COMP | N2PSA1FI-DRA | N2PSA1P-COMP | N2PSA1T-IN | N2PSA1T-OUT | N2PSA1COMP-2FOX | N2PSA1PG-9 | N2PSA1PN2-OUT | N2PSA1ACT-DOX | N2PSA1PG2A | N2PSA1PG2B | N2PSA1RV6 | N2PSA1RV70 | N2PSA1PAIR-2F | N2PSA1PN2-2F | N2PSA1AC-O2
項目 | 2F新設COMP. STOP SERY項目-有無(控制面板) | 2F新設COMP.吐出壓力(控制面板) | 2F新設COMP.運行時間(控制面板) | 2F新設COMP.環境溫度(控制面板) | 2F新設COMP.中間壓力(控制面板) | 2F新設COMP.油循環壓力(控制面板) | 2F新設COMP.1級排氣溫度(控制面板) | 2F新設COMP.2級進氣溫度(控制面板) | 2F新設COMP.2級排氣溫度(控制面板) | 2F新設COMP.油循環溫度(控制面板) | 2F新設COMP.狀態-有無警報(控制面板) | 2F新設COMP.油霧分離器真空指示器-紅色是否消失 | 2F新設COMP.油霧分離器操作壓力 | 2F新設COMP.DRAIN狀態 | 2F新設COMP.Air Dryer DRAIN狀態 | 氮發生器1 COMP.冷卻水流量 | 氮發生器1 除濕機冷卻水流量 | 氮發生器1 COMP.Air (2F)壓力 | 氮發生器1 除濕機入口-Air溫度 | 氮發生器1 除濕機出口-Air溫度 | 氮發生器1 U.P.W液面(2F)COMP.狀態-閥開 | 氮發生器1 P.S.A入口-Air壓力 | 氮發生器1 P.S.AN2-吐出壓力 | 氮發生器1 DRAINSPEA狀態-上限以下 | 氮發生器1 空氣入口壓力 | 氮發生器1 空氣入口壓力 | 氮發生器1 製品N2流量 | 氮發生器1 空氣入口減壓 | 氮發生器1 AirTANK壓力(2F) | 氮發生器1 N2TANK壓力(2F) | 氮發生器1 酸素濃度
管理值 | =O | 0.5~0.7 |  | <45 | 0.15~0.26 | 0.11~0.18 | <224 | <67 | <234 | <67 | =X | =O | 0.15~0.18 | =O | =O | >10 | <2 | 6~9 | <50 | <20 | =O | 6~9 | 4~5 | =O | 6~9 | 6~9 | <130 | 3.5~4.5 | 6~9 | 5~7 | <1000
單位 | O X | MPa | h | oC | MPa | MPa | oC | oC | oC | oC | O X | O X | MPa | O X | O X | m3/h | m3/h | kgf/cm2 | oC | oC | O X | kgf/cm2 | kgf/cm2 | O X | kgf/cm2 | kgf/cm2 | Nm3/h | kgf/cm2 | kgf/cm2 | kgf/cm2 | ppm